## Registers
xG-18
Registers | [6 empty] | v1.0.0
Register Address | R/W | Data Type | Content |  |  | Bit Nr. | Category
0 | R | MixedBits | Master Watchdog | MWD Enable |  | 0 | Advanced
|  |  |  | MWD Reboot detection |  | 1
1 | R | INT | Temperature | CH1 |  |  | Basic
2 | R | INT | T = reg/100 | CH2 |  |  | Basic
3 | R | INT |  | CH3 |  |  | Basic
4 | R | INT | Negative temperatures are in the two's complement (signed integer - 16 bit) | CH4 |  |  | Basic
5 | R | INT |  | CH5 |  |  | Basic
6 | R | INT |  | CH6 |  |  | Basic
7 | R | INT |  | CH7 |  |  | Basic
8 | R | INT |  | CH8 |  |  | Basic
9 | R | MixedBits | Temperature | CH1 validity value |  | 0 | Basic
|  |  |  | CH2 validity value |  | 1
|  |  |  | CH3 validity value |  | 2
|  |  |  | CH4 validity value |  | 3
|  |  |  | CH5 validity value |  | 4
|  |  |  | CH6 validity value |  | 5
|  |  |  | CH7 validity value |  | 6
|  |  |  | CH8 validity value |  | 7
1000 | R | Word | Firmware Version |  |  |  | Expert
1001 | R | Word | Number of I/Os |  |  |  | Advanced
|  |  | Number of DIs |  |  | 0 - 7
|  |  | Number of DOs |  |  | 8 - 15
1002 | R | Word | Number of peripherals |  |  |  | Advanced
|  |  | Number of internal RS485 lines |  |  | 0 - 3
|  |  | Number of AOs |  |  | 4 - 7
|  |  | Number of AIs |  |  | 8 - 15
1003 | R | Word | Firmware ID |  |  |  | Expert
1004 | R | Word | Hardware ID |  |  |  | Expert
1005 - 1006 | R | DWord | PCB Serial Number |  |  |  | Expert
1007 | RW | Word | Interrupt Mask |  |  |  | Expert
|  |  | RS485 RX queue not empty |  |  | 0
|  |  | RS485 TX queue empty |  |  | 1
|  |  | RS485 ModBus RX frame finished |  |  | 2
|  |  | Digital Input changed state |  |  | 3
1008 | RW | Word | MasterWatchDog (MWD) Timeout (in 1ms) |  |  |  | Advanced
1009 | R | Word | VRef of MCU |  |  |  | Expert
1010 | RW | INT | Measuring interval | CH1 | in seconds |  | Basic
1011 |  |  |  | CH2 |  |  | Basic
1012 |  |  |  | CH3 |  |  | Basic
1013 |  |  |  | CH4 |  |  | Basic
1014 |  |  |  | CH5 |  |  | Basic
1015 |  |  |  | CH6 |  |  | Basic
1016 |  |  |  | CH7 |  |  | Basic
1017 |  |  |  | CH8 |  |  | Basic
1018 | RW | MixedBits | RS4851.1 Configuration |  |  |  | Advanced
|  |  | Baud rate (1110₂ = 14₁₀ = 19200, 1101₂ = 13₁₀ = 9600) |  |  | 0 - 12
|  |  | Parity enable |  |  | 13
|  |  | Parity-0=Even, 1=Odd |  |  | 14
1019 | RW | MixedBits | Modbus Address Configuration (1-255) |  |  |  | Advanced

## Coils
xG-18
Coils
Register Address | R/W | Content | Category
1000 | R | MWD reset indication | Advanced
1002 | RW | Reset MCU | Advanced
1003 | RW | Save current configuration and use on startup | Advanced
1004 | RW | Firmware programming toggle | Expert
1005 | RW | Firmware reprogramming toggle | Expert
1006 | RW | Firmware calibration programming toggle | Expert

## Description
Check out the UniPi Knowledge base for more information
Firmware (re)programming tool - Extension FW update tool
Byte order
0-LSB, 15-MSB
Baud rate | Configuration
Value | Speed [bps]
11 | 2400
12 | 4800
13 | 9600
14 | 19200
15 | 38400
4097 | 57600
4098 | 115200